## Slide 1: Guinea Energy Intelligence 2026
Power-sector assessment, investment pipeline and priorities for 2027–2035
Public/Government Edition — v1.3 (draft for owner review; not approved; not published)
Executive presentation · 16-Oct-2026
Prepared by Alendei Green RE Pvt. Ltd. (Alendei Group), Vadodara, India
Evidence-led research submission; not a government-approved dataset · Evidence retrieved 08–15 October 2026

## Slide 2: Large hydro base, but the system is not yet firm
Guinea was a net exporter in 2025, a wet year. Dry-season firm supply, the Conakry grid and utility finances are the binding constraints.
1,305.6 MW
Installed capacity, 2025 (hydro 787.7 · thermal 518)
≈1,000 MW
'Reliably available' (World Bank; term undefined)
961 MW
Peak load served, May 2025 (334 MW in 2017)
903 GWh
Exports, 2025 (EDG table; unit not stated)
53.8%
Access 2024 · rural 29.4%
¢10 vs ¢27
US¢/kWh: average tariff vs cost of service
≈379 MW
Nameplate under construction or financed; none commissioned
US$8.9 bn
Still to raise of the US$11.47 bn compact need
Sources: Électricité de Guinée [79]; World Bank [64]; World Bank [69]; Government of Guinea [22]; Ministère de l'Énergie, republished by Mediaguinee [33]; Guinéenews [30]; Islamic Development Bank / Gouvernement de Guinée [32]; Électricité de Guinée for the Ministère de l'Énergie [80]; ECOWAS Bank for Investment and Development [11]; ECOWAS Bank for Investment and Development [13]; ECOWAS Bank for Investment and Development [12]. [n] = reference list at end.

## Slide 3: Served demand has nearly tripled since 2017
Chart: Peak load served, interconnected grid (MW)
| 2016 | 2017 | 2022 | 2024 | 2025
Peak load served (MW) | 295 | 334 | 513 | 829 | 961
Peak served reached 961 MW in May 2025 (late dry season); earlier annual peaks fell around 21:00.
The World Bank describes about 1,000 MW as 'reliably available' without defining the term, so no reserve margin can be derived.
No seasonal dependable capacity is documented for any hydro plant.
2024 drought: 129,797 hours of load shedding for production deficit; energy not distributed 543–794 GWh (two EDG figures conflict).
Sources: Électricité de Guinée [75]; World Bank [64]; Électricité de Guinée [79]; Électricité de Guinée [78]. Served load is not underlying demand. [n] = reference list at end.

## Slide 4: One river drives supply, and its flow swings 70-fold
Chart: Konkouré at Kaléta: natural mean monthly flow (m³/s), 1948–1993
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
m³/s | 68.7 | 38.4 | 22.2 | 18 | 34.8 | 136 | 506 | 1250 | 1090 | 664 | 309 | 126
Natural flow ranges from 18 m³/s in April to 1,250 m³/s in August; about 90% of runoff falls June–November.
Souapiti, Kaléta and Garafiri share one river, with no published cascade operating rules.
The 2024 drought cut hydro output by more than 10%.
Climate projections (World Bank): hydro output in 2050 from −30% to +25%.
Sources: Groupement d'Intérêt Economique ORSTOM-EDF, for Ministère des Ressources Naturelles, des Energies et de l'Environnement [23]; World Bank [64]; World Bank Group [71]. [n] = reference list at end.

## Slide 5: Grid works are financed but slow to deliver
Line / project | Evidenced stage | Status
Manéah–Linsan 225 kV | Financing committed | AFD EUR 80 m; 41% disbursed; 8% site progress (end-2025)
Linsan–Fomi 225 kV | Financing committed | EIB EUR 170 m signed 2021; no works start evidenced
Guinea–Mali 225 kV | Under construction, delayed | ~85% progress on World Bank-financed works; US$380.8 m approved in total
OMVG and CLSG regional loops | Operating | Transmission-fee arrears US$57 m (June 2026)
Conakry substations | Constraint | Transformer loading ≈80–103% (EDG table; year 2022 or 2023 ambiguous)
Sources: Électricité de Guinée [79]; European Investment Bank [18]; World Bank [66]; World Bank [65]; World Bank [67]; Électricité de Guinée SA [82]. [n] = reference list at end.

## Slide 6: The utility sells at about a third of its cost
Chart: US¢ per kWh (World Bank estimates, 2025)
| Average tariff | Cost of service
US¢/kWh | 10 | 27
GNF −430 bn
EDG-reported net result, 2025 (no audit opinion located)
55%
Subsidies as share of revenue, 2019–2023
GNF 6,500 bn
Payables to independent producers, 2023
30%
Losses 2024; 40% commercial (2025); bases differ
Electricity law of 1993 still in force · regulator not fully operational · PPA currency terms undocumented
Sources: World Bank [64]; Électricité de Guinée [79]; Government of Guinea [22]; Électricité de Guinée / MEHH [81]. Verify with a qualified professional before acting. [n] = reference list at end.

## Slide 7: 2030 demand: strong growth, uncertain scale
Chart: Peak demand, MW (illustrative scenarios)
| 2025 reported (peak served) | 2030 A: trend (estimate) | 2030 B: national plan
MW | 961 | 1860 | 3894
A: ≈1,860 MW, the 2017–2025 growth rate (14.1% a year) extended. An arithmetic illustration only.
B: 3,894 MW national plan (via the Mission 300 compact): 1,635 MW domestic, 1,442 MW mining, 817 MW exports; mining and export loads are not contracted with the grid.
Mining today requires ≈558 MW, mostly from captive plant.
Installed 1,305.6 MW + ≈379 MW under construction or financed ≈ 1,684 MW nameplate (not dependable).
Sources: Électricité de Guinée [79]; Électricité de Guinée [74]; Government of Guinea [22]; World Bank [64]; West African Power Pool / ECOWAS [54]. [n] = reference list at end.

## Slide 8: Resource and technology options on the evidence
Hydro
Technical potential 6,233 MW (national atlas). Dependable output undocumented; transboundary and resettlement limits.
Solar PV
Modelled resource values withheld pending licence confirmation. No grid plant verified as operating; no hosting study located.
Storage
A WAPP/GIZ study recommends 13.2 MW, 1 h for frequency reserve (one grid service; not an adopted requirement).
Thermal / gas
Firm and dispatchable, but uses imported fuel oil; LNG-to-power announced only.
Wind
Weak modelled resource (3.8 m/s at 100 m, Global Wind Atlas); no measurements.
Mini-grids
Rural plan: 714 localities for mini-grids, 1,326 for solar kits; GNEAP-2 funds 26 mini-grids.
Sources: Ministère de l'Énergie et de l'Hydraulique, Guinea / World Bank [35]; Government of Guinea [22]; West African Power Pool / GIZ PROCEM II [55]; DTU Wind Energy / World Bank Group [10]; World Bank [64]; Électricité de Guinée [79]. Wind values are model estimates, not ground measurements; modelled solar-resource values withheld pending licence confirmation. [n] = reference list at end.

## Slide 9: ≈379 MW under construction or financed
Chart: Stated nameplate MW by evidenced stage (estimate aggregation)
| Operating | Under construction | Financing committed | Active development | Announced | Proposed
Hydro | 787.7 | 300 | 38.6 | 955.5 | 0 | 1731.1
Thermal (incl. gas) | 518 | 0 | 40 | 0 | 1938 | 600
Solar PV | 0 | 0 | 0 | 90 | 107 | 996
Under construction: Amaria 300 MW (61% overall execution, delayed); online year 2027 per the compact.
Signed financing, no construction start evidenced: Kankan 40 MW; EBID micro-hydro 27.6 MW; Tinkisso 2 11 MW. None commissioned.
Covers identified projects with a stated capacity only; not a commissioning forecast.
Kamissaya 50 MWc solar: financing and works reported by the press only.
Sources: Government of Guinea [22]; Ministère de l'Énergie, republished by Mediaguinee [33]; Guinéenews [30]; Électricité de Guinée [79]; Islamic Development Bank / Gouvernement de Guinée [32]; Électricité de Guinée for the Ministère de l'Énergie [80]; ECOWAS Bank for Investment and Development [11]; ECOWAS Bank for Investment and Development [13]; ECOWAS Bank for Investment and Development [12]; Financial Afrik [20]. Nameplate, not dependable capacity; mixed AC/DC bases. [n] = reference list at end.

## Slide 10: Financing needs far exceed commitments
Chart: Mission 300 compact need by segment, US$ bn (requested)
| Generation | Rural electrification | Transmission | Distribution
US$ bn | 5.33 | 3.18 | 1.74 | 1.13
US$11.47 bn
Total need 2025–2030
US$8.90 bn
Still to raise
Announced is not committed. The compact's US$2.56 bn 'mobilised or in progress' mixes signed loans with items that have no agreement. No World Bank Group energy guarantee is in use; OECD country-risk class 7; recent large generation relied on sovereign-backed Chinese debt.
Sources: Government of Guinea [22]; African Trade & Investment Development Insurance [4]; World Bank Group [72]; OECD [39]; AidData, William & Mary [7]. Segments as listed sum to US$11.37 bn. [n] = reference list at end.

## Slide 11: The choice: dependable, deliverable, sustainable supply
Thesis. Guinea should establish dependable, deliverable and financially sustainable electricity supply before committing to a predetermined generation mix.
A sequencing recommendation from the evidence, not a completed least-cost optimisation.
Transmission execution is binding
Linsan–Fomi financed in 2021, no works; Manéah–Linsan 8% site progress; Conakry transformers ≈80–103% loaded (EDG table, year ambiguous).
EVIDENCE
La Côtière: stated purpose and inferred effect
Compact purpose: evacuate Kaléta–Souapiti output and supply mines (US$771 m to mobilise). Effect on dispatch: research inference, not modelled.
EVIDENCE + INFERENCE
Solar scale-up: grid integration not yet quantified
No hosting or evacuation limit published; compact itself cites evacuation and stability constraints; land, payment security and procurement also bind.
EVIDENCE
Storage services differ; seasonal deficits need firm energy
Frequency response, short power support and evening-peak shifting are battery services; multi-week drought deficits are not. 13.2 MW/1 h is a study figure for frequency reserve only.
ESTIMATE
A few delays outweigh the pipeline size
Amaria = 300 of the ≈379 MW subset under construction or financed (79%; 300 ÷ 378.6), delayed. The ≈6.4 GW gross list is not expected generation.
ESTIMATE
A first private renewable deal could set the precedent
No grid solar plant operates; no energy guarantee in use; PPA currency undocumented.
HYPOTHESIS
Sources: European Investment Bank [18]; Électricité de Guinée [79]; Électricité de Guinée SA [82]; Government of Guinea [22]; West African Power Pool / GIZ PROCEM II [55]; Ministère de l'Énergie, republished by Mediaguinee [33]; World Bank Group [72]. Battery comparison is illustrative scale only (13.2 MWh vs 542,767.5 MWh), not a sizing calculation. [n] = reference list at end.

## Slide 12: Five national priorities, in dependency order
P1
Deliver financed transmission
Complete Linsan–Fomi, Manéah–Linsan and Guinea–Mali; reinforce Conakry substations; close financing for La Côtière.
Depends on: Financing largely exists
Gate: Works schedules published; contracts awarded; La Côtière financing decided
P2
Establish a firm-capacity baseline
Measure plant-level seasonal dependable capacity, adopt cascade operating rules, analyse dry-year hydrology and publish an hourly load curve.
Depends on: Data sharing by EDG and plant companies
Gate: Dependable-capacity study and load curve published
P3
Restore payment discipline
Adopt an arrears plan for independent producers, enforce payment of public-administration bills, scale metering and secure guarantees for new contracts.
Depends on: Budget decisions
Gate: Arrears plan adopted; guarantee eligibility confirmed
P4
Procure capacity technology-open, at least cost
Procure firm evening and dry-season capacity through a technology-open least-cost process, including renewables and storage where grid integration, firmness and price justify them.
Depends on: P2 sizing, P1 evacuation, P3 bankability
Gate: Least-cost plan and grid-integration study; transparent tender framework
P5
Decide industrial supply and regional trade
Decide how mines and refineries are supplied (grid, shared or hybrid captive) and how connection costs are shared; strengthen WAPP trade and settlement.
Depends on: P1, P2
Gate: Mining-supply policy; connection-cost rules
Why this order
P4 is sized on P2, limited by P1 evacuation and made bankable by P3; P5 follows P1 and P2. A fixed technology volume should wait for P2 and a grid-integration study. Sequencing, not a least-cost optimisation.
Priorities are technology-neutral sequencing recommendations drawn from the evidence; they are not official decisions.

## Slide 13: Disposition, roadmap and decision gates
Disposition | Projects and technologies
Complete and deliver | Financed transmission (Linsan–Fomi, Manéah–Linsan, Guinea–Mali); Amaria with its evacuation; financed small hydro (EBID micro-hydro, Tinkisso 2) with dependable output documented.
Verify status before planning on it | Kamissaya/Kindia 50 MWc (scope and financing reported inconsistently); Khoumagueli 40 MWac (milestones missed); Kankan 40 MW HFO (works not tendered as of Jan-2026).
Study before committing | Konkouré cascade dependable capacity and operating rules; grid integration and hosting; storage beyond frequency reserve; wind (no measurements); mining-load supply options.
Defer new commitments | Next large hydro until dependable output, transboundary approvals and resettlement are documented; LNG-to-power until feasibility and gas-price evidence exist.
Plan-level only | About 1 GW of compact solar listings and other announced or proposed projects (possible duplicates).
Horizon | Government, EDG and regulator
0–12 months | Works schedules (P1); dependable-capacity study and load curve (P2); arrears plan (P3); GNEAP-2 mini-grid selection
1–3 years | Grid-integration study; least-cost plan; tender framework; La Côtière financing; Amaria commissioning
3–5 years | Competitive procurement of firm and renewable capacity; regulator operational
5–10 years | Next large hydro chosen on dependable output; grid code; third-party access
N1
Works schedules published and contracts awarded for financed lines
N2
Plant-level dependable capacity and an hourly load curve published
N3
Arrears plan adopted; guarantee eligibility confirmed
N4
Least-cost plan and grid-integration study completed; tender framework issued
N5
Policy on mining supply and connection-cost sharing adopted
Sources: project documents cited per project in the online platform (Projects tab) and the reference list at the end. Qualified readings of current evidence; not investment recommendations or official decisions. Planning horizons, not confirmed schedules.

## Slide 14: Prioritised action plan
Immediate (12 months)
Konkouré cascade dependable-capacity and rules study
Unblock financed works: Linsan–Fomi, Manéah–Linsan, Kankan
Producer-arrears plan and public payment discipline
Technology-open firm-capacity procurement
Assess a 13.2 MW reserve battery (study)
Publish load curve; reconcile 2024 data
2027–2029
Complete Conakry reinforcement and backbone lines
Commission Amaria with evacuation
Hosting study, then competitive solar with storage
Metering, loss reduction, tariff path
GNEAP-2 mini-grids; mini-grid regulation
Moribaya fuel depot; fuel cost transparency
To 2035
Next large hydro chosen on dependable output
Supply solutions for mining and refinery loads
New electricity law, regulator, grid code, third-party access
Deeper WAPP trade; secure settlement
Hydrological monitoring and climate-risk planning
Priorities follow from the evidence on the preceding slides and in the online platform; they are technology-open and are not investment recommendations.

## Slide 15: Who contributes what
Government
Framework, tariff path, payment discipline, land and permits, transparent procurement, data publication
EDG
Dispatch and cascade operation, metering, loss reduction, collections, project delivery
AREE (regulator)
Tariff orders, licensing, grid code aligned with the regional code, dispute resolution
Development partners
Concessional grid and access finance, guarantees (none yet used in energy), preparation, technical assistance
Private investors
Generation and storage, EPC and O&M, mini-grid concessions, mining-load supply, once payment security exists
About the sponsor. This research was prepared by Alendei Green RE Pvt. Ltd. (Alendei Group, Vadodara, India), a company with a commercial interest in Guinea's energy sector. Alendei describes its activities as solar EPC, commercial and industrial solar, battery integration and renewable project development, mainly in India; these capabilities have not been independently verified in this research. Alendei has no project, office, licence, partnership or financing commitment in Guinea. Any future participation would be through competitive procurement or commercial agreements and is not implied by this material. The national findings and priorities were established before private-sector roles were considered and are technology-neutral.

## Slide 16: Key risks and dependencies
Risk | Rating | Mitigation
Dry-season supply shortfall | High | Cascade study; firm capacity; storage; imports
Delivery of financed works | High | Project delivery unit; published schedules; development-partner supervision
Utility finances and arrears | High | Tariff path; arrears plan; loss reduction
Climate and hydrological variability | High | Monitoring; diversification; spillway reviews
Fuel supply disruption | Medium | Moribaya depot; reserve stocks; diversification
Financing and country risk | Medium–High | Guarantees; concessional blending; transparent PPAs
Transboundary and environmental/social constraints | Medium | Early impact assessment; basin consultation
Data gaps and conflicting statistics | Medium | Data reconciliation; publication of load curves
Ratings are the preparer's qualitative judgement based on the evidence cited in this presentation; they are not an official risk assessment.

## Slide 17: Decisions needed and evidence to obtain
Decisions for the authorities
Mandate the cascade dependable-capacity study and data sharing
Set up a delivery unit for financed works, with public schedules
Approve an arrears plan and tariff trajectory
Launch technology-open firm-capacity and solar procurement frameworks
Request development-partner guarantees and preparation support
Material evidence gaps
Seasonal dependable capacity of every hydro plant
Daily load curve; suppressed demand
PPA currency and payment terms; arrears by producer
Primary terms of the largest loans (Souapiti, Amaria)
Delivered fuel cost after 2019
Conflicting 2024 statistics (exports, billed, unserved energy)
Conflicting statistics and gaps are listed with their sources in the online platform (Risks & gaps tab).

## Slide 18: Build firmness, deliver what is financed, restore the utility
Interactive platform with all figures, projects and numbered sources accompanies this presentation.
Evidence-led research submission · not a government-approved dataset · not reviewed or endorsed by any government or cited institution.
Evidence retrieved 08–15 October 2026 · verify legal, financial, tariff and regulatory points with a qualified professional before acting.
Figures have not been independently verified by a human subject-matter expert.
Prepared by Alendei Green RE Pvt. Ltd. (Alendei Group), Vadodara, India · 16-Oct-2026

## Slide 19: References (1 of 3)
[4] African Trade & Investment Development Insurance (ATIDI, formerly ATI) (n.d.). Investor Relations - Member States (African Trade & Investment Development Insurance, ATIDI). https://www.atidi.africa/investor-relations/member-states/
[7] AidData, William & Mary (Chinese Loans and Grants dataset) (n.d.). China Eximbank provides $1.175 billion buyer's credit loan for 450MW Souapiti Hydroelectric Power Plant Construction Project (AidData record ID 187). https://china.aiddata.org/projects/187
[10] DTU Wind Energy / World Bank Group (ESMAP) (12-Jun-2025). Global Wind Atlas – country layers for Guinea (mean wind speed at 100 m). https://globalwindatlas.info/
[11] ECOWAS Bank for Investment and Development (EBID/BIDC) (11-Nov-2025). EBID signs EUR 123.451 million facility to advance agricultural education and rural electrification in the Republic of Guinea. https://www.bidc-ebid.org/en/?p=278382
[12] ECOWAS Bank for Investment and Development (EBID/BIDC) (12-Aug-2026). EBID commits over USD 510 million to drive development across West Africa (100th Board Meeting). https://www.bidc-ebid.org/en/ebid-commits-over-usd-510-million-to-drive-development-across-west-africa/
[13] ECOWAS Bank for Investment and Development (EBID/BIDC) (14-Sep-2026). EBID commits EUR 269.5 million to development in the Republic of Guinea. https://www.bidc-ebid.org/en/ebid-commits-eur-269-5-million-to-development-in-the-republic-of-guinea/
[18] European Investment Bank (23-Apr-2021). 330 millions d'EUR de l'Equipe Europe a la construction de la nouvelle ligne electrique de 225 kV Guinee-Mali (press release 2021-138-FR). https://www.eib.org/fr/press/all/2021-138-330-millions-d-eur-de-l-equipe-europe-a-la-construction-de-la-nouvelle-ligne-electrique-de-225-kv-guinee-mali-qui-approvisionnera-en-energie-propre-et-abordable-des-millions-de-personnes-en-afrique-de-l-ouest
[20] Financial Afrik (24-Apr-2026). Guinée : Cegelec décroche la construction d'une centrale solaire de 50 MWc. https://www.financialafrik.com/2026/04/24/guinee-cegelec-decroche-la-construction-dune-centrale-solaire-de-50-mwc/
[22] Government of Guinea (published by the World Bank, M300 energy compacts) (2025). Pacte National de l'Énergie pour la République de Guinée (Mission 300 National Energy Compact). https://thedocs.worldbank.org/en/doc/e8d7d425ed2300100ec9574759a5590d-0010012025/original/Guinea-Compact-M300.pdf
[23] Groupement d'Intérêt Economique ORSTOM-EDF, for Ministère des Ressources Naturelles, des Energies et de l'Environnement (Guinée) (Jul-1994). Aménagement hydro-électrique de Kaléta sur le Konkouré - Synthèse des données de base - Hydrologie. https://horizon.documentation.ird.fr/exl-doc/pleins_textes/divers17-01/010024879.pdf
[30] Guinéenews (reproducing presidential decree of 25-Apr-2026) (26-Apr-2026). Guinée : le projet de construction de la Centrale hydroélectrique d'Amaria (300 MW) déclaré « Projet d'Intérêt National » (décret intégral). https://guineenews.org/2026/04/26/guinee-la-construction-de-la-centrale-hydroelectrique-damaria-declaree-projet-dinteret-national-decret/

## Slide 20: References (2 of 3)
[32] Islamic Development Bank (project procurement portal) / Gouvernement de Guinée (Apr-2025). Avis général de passation des marchés (AGPM) - Projet de construction d'une centrale thermique de 40 MW à Kankan et de réhabilitation et d'extension du réseau MT/BT de Kouroussa et seize localités. https://www.isdb.org/project-procurement/sites/pproc/files/2025-05/AGPM-Projet%20Kankan-Kouroussa-%20Avril%202025%20%28002%29.docx
[33] Ministère de l'Énergie (Cellule de communication), republished by Mediaguinee (14-Jul-2026). Barrage hydroélectrique d'Amaria : le ministre de l'Énergie salue l'avancement satisfaisant des travaux. https://mediaguinee.com/2026/07/%F0%9D%90%81%F0%9D%90%9A%F0%9D%90%AB%F0%9D%90%AB%F0%9D%90%9A%F0%9D%90%A0%F0%9D%90%9E-%F0%9D%90%A1%F0%9D%90%B2%F0%9D%90%9D%F0%9D%90%AB%F0%9D%90%A8%F0%9D%90%9E%F0%9D%90%A5%F0%9D%90%9E%F0%9D%90%9C
[35] Ministère de l'Énergie et de l'Hydraulique (MEH), Guinea / World Bank (prepared by AECOM) (15-Feb-2018). Study for the Development of a Hydropower Resources Atlas of Guinea - Final Report (Atlas Report Phase 3, Revision 1).
[39] OECD (26-Jun-2026). Country Risk Classifications of the Participants to the Arrangement on Officially Supported Export Credits (valid as of 26 June 2026). https://www.oecd.org/content/dam/oecd/en/topics/policy-sub-issues/country-risk-classification/cre-crc-current-english.pdf
[54] West African Power Pool (WAPP) / ECOWAS (consultant-prepared, Tractebel) (Dec-2018). Update of the ECOWAS revised master plan for the development of power generation and transmission of electrical energy - Final Report - Volume 2: State of play of the current situation of the electricity system and perspectives. https://www.ecowapp.org/sites/default/files/volume_2.pdf
[55] West African Power Pool (WAPP) / GIZ PROCEM II (consultant report) (24-Jun-2024). Development of a least cost investment plan and regulatory frameworks for BESS deployment in West Africa (WAPP grid) - Report on BESS's Lower-Cost Investment Plan (6279-BESS-RP-006, Rev. R4 FINAL). https://www.ecowapp.org/sites/default/files/1bess_investement_plan_fv_en.pdf
[64] World Bank (06-Jun-2025). Guinea – Second Phase of the Electricity Access Scale Up Project (P511453): Project Appraisal Document. https://documents.worldbank.org/curated/en/099080425213535308/text/BOSIB-e7b1cb57-9078-490e-8988-30bc9fe608c0.txt
[65] World Bank (17-Dec-2025). Restructuring Paper on a Proposed Project Restructuring of Guinea - Mali Interconnection Project. https://documents.worldbank.org/curated/en/099121625205531404/pdf/P166042-10e30b22-6151-4c15-8c67-b3c75a6ddb03.pdf
[66] World Bank (11-May-2026). Disclosable Version of the ISR - Guinea - Mali Interconnection Project - P166042 - Sequence No: 13. https://documents.worldbank.org/curated/en/099051126091010144/pdf/P166042-48ef2d03-2ed3-4e71-9237-8d147dbc496e.pdf
[67] World Bank (25-Jun-2026). Implementation Completion and Results Report: OMVG Interconnection Project (P146830). https://documents.worldbank.org/curated/en/099062426204526346/pdf/BOSIB-6b92f372-724e-4687-9ef0-da35498f0056.pdf
[69] World Bank (13-Jul-2026). World Development Indicators: Access to electricity (% of population), urban, rural — Guinea (API extract) + series metadata. https://data.worldbank.org/indicator/EG.ELC.ACCS.ZS?locations=GN

## Slide 21: References (3 of 3)
[71] World Bank Group (Dec-2025). Guinea - Country Climate and Development Report. https://documents1.worldbank.org/curated/en/099021226050013303/pdf/P501474-e1a9833f-7eb7-4b58-bee2-81c8ab479282.pdf
[72] World Bank Group (Jun-2026). Guinea Country Partnership Framework – Annex 3: Financing and Implementation Arrangements. https://documents1.worldbank.org/curated/en/099802106252635272/pdf/SECBOS-5a27d0cd-0524-4e7c-8f00-0e44094e6890.pdf
[74] Électricité de Guinée (EDG / EDG-SA) (n.d.). Électricité de Guinée - Rapport annuel 2017. https://edg.com.gn/wp-content/uploads/2024/07/RAPPORT-ANNUEL-EDG-2017_VF.pdf
[75] Électricité de Guinée (EDG / EDG-SA) (17-Mar-2022). Électricité de Guinée - Rapport annuel 2021. https://edg.com.gn/wp-content/uploads/2023/02/RAPPORT-2021_EDG-MEP1_definitif_17032022.pdf
[78] Électricité de Guinée (EDG / EDG-SA) (Jul-2025). Électricité de Guinée - Rapport annuel 2024. https://edg.com.gn/wp-content/uploads/2025/07/Rapport-annuel-exercice-2024.pdf
[79] Électricité de Guinée (EDG / EDG-SA) (Aug-2026). Électricité de Guinée - Rapport annuel 2025. https://edg.com.gn/wp-content/uploads/2026/08/RAPPORT-ANNUEL-EDG-2025-Vf.pdf
[80] Électricité de Guinée (EDG-SA) for the Ministère de l'Énergie (21-Jan-2026). Appel à manifestation d'intérêt - Contrôle et supervision des travaux de construction de la centrale thermique HFO de 40 MW à Kankan (Financement BID GIN-1057). https://edg.com.gn/wp-content/uploads/2026/01/20250722_161811_BID-Avis_a_Manifestation_dinteret_Centrale_thermique_40_MW.pdf
[81] Électricité de Guinée / MEHH (16-Dec-2024). Avis à manifestation d'intérêt – L'actualisation et la finalisation du Projet de loi cadre du secteur de l'Energie et ses textes d'application (PPF BAD). https://edg.com.gn/wp-content/uploads/2024/12/Guinee_PPF-energie_AMI_Loi_cadre_VFii_BAD.pdf
[82] Électricité de Guinée SA (Feb-2025). Rapport annuel 2023 – EDG-SA (Rapport d'activités exercice 2023). https://edg.com.gn/wp-content/uploads/2025/02/RAPPORT-ACTIVITES-EDG-SA-Excercice-2023.pdf